| Port Monmouth Library  Middletown Township (N.J.)  ADA Transition Plan 168 Main St. (Port Monmouth) Spring 2008 |
| --- |
| Location | Identified Barrier(s) | Recommended Corrective Action Based on ADAAG or Applicable Guideline | Priority: L=Low M=Medium H=High | *Cost Estimate | Barrier Removal Target Date & Notes |
| EXTERIOR FEATURES |
| Parking | One space is signed as accessible but no “van accessible” designation exists. No access aisle exists and the space is not on the shortest route to the entrance. | At least 1 accessible space shall be designated as “van accessible” and be served with an access aisle at least 96” wide. Signs shall be located so they cannot be obscured by a vehicle parked in the space. Accessible parking spaces serving a particular building shall be located on the shortest accessible route of travel from adjacent parking to an accessible entrance (4.1.2(5)(b) & 4.6). | H | $500 |  |
| Entrance | The entrance has numerous barriers such as: Sloped ground surface in the exterior maneuvering clearance( Inadequate maneuvering clearance width (3”) on pull side of door. Door handle requires pinching and grasping to operate. Entrance has a 1” threshold. | The floor or ground area within the required maneuvering clearances shall be level and clear (4.13.6 & Figure 25). Front approaches to pull side of swinging doors shall have maneuvering space that extends from the hinge side of the door to 18” minimum, 24” preferred, beyond the latch side of the door and 60” minimum perpendicular to the doorway (Figure 25(a)). Handles, pulls, latches, locks, and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate (4.13.9). Thresholds at doorways shall not exceed ½” beveled (4.13.8). | H H H H | $2,500 $500 $50 $200 |  |
|  |  | INTERIOR FEATURES |  |  |  |
| Miscellaneous Rooms and Spaces | Exit signs are not in accessible locations or formats. | Where permanent identification is provided for rooms and spaces, signs shall be installed on the wall adjacent to the latch side of the door. Where there is no wall space to the latch side of the door, signs shall be placed on the nearest adjacent wall. Mounting height shall be 60’ above the finish floor to the centerline of the sign. Mounting location for such signage shall be so that a person may approach within 3” of signage without encountering protruding objects or standing within the swing of a door. Letters and numerals shall be raised 1/32”, upper case, sans serif or simple serif type and shall be accompanied with Grade 2 Braille (4.30.4 & 4.30.6). | H | $150 |  |
| Miscellaneous | Numerous book shelves exceed maximum height for reach ranges. | Recommendation: install signage directing patrons to contact library staff for assistance in obtaining materials if needed. | M | $100 |  |
| Public Restrooms | Men’s: Sign is located on the door. The maneuvering clearance width on pull side of door is 9”. The urinal is 22” high to rim. The accessible toilet stall has a turn type lock and the toilet flush control is located on far side of toilet. Women’s: Sign is located on the door. The maneuvering clearance width on pull side of door is 14”. The accessible toilet stall has a turn type lock. | Where permanent identification is provided for rooms and spaces, signs shall be installed on the wall adjacent to the latch side of the door. Mounting height shall be 60’ above the finish floor to the centerline of the sign. Mounting location for such signage shall be so that a person may approach within 3” of signage without encountering protruding objects or standing within the swing of a door (4.30.6). Front approaches to pull side of swinging doors shall have maneuvering space that extends from the hinge side of the door to 18” minimum, 24” preferred, beyond the latch side of the door and 60” minimum perpendicular to the doorway (Figure 25(a)). Urinals shall be stall-type or wall-hung with an elongated rim at a maximum of 17” above the finish floor. Flush controls shall be mounted no more than 44” above the finish floor (4.18). Handles, pulls, latches, locks, and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Flush controls shall be mounted on the wide side of toilet areas (4.13.9 & 4.16.5). Where permanent identification is provided for rooms and spaces, signs shall be installed on the wall adjacent to the latch side of the door. Mounting height shall be 60’ above the finish floor to the centerline of the sign. Mounting location for such signage shall be so that a person may approach within 3” of signage without encountering protruding objects or standing within the swing of a door (4.30.6). Front approaches to pull side of swinging doors shall have maneuvering space that extends from the hinge side of the door to 18” minimum, 24” preferred, beyond the latch side of the door and 60” minimum perpendicular to the doorway (Figure 25(a)). Handles, pulls, latches, locks, and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate (4.13.9). | M+ M L L+ M+ M L+ | $0 $500 $1,500 $350 $0 $500 $50 |  |

There is a ramped slope at the library entrance and

inadequate maneuvering clearance.

| Priority Level | Cost Estimate Totals |
| --- | --- |
| Low’s | $1,900 |
| Medium’s | $1,100 |
| High’s | $3,900 |
| TOTAL | $6,900.00* |

* Cost estimates are given as general guidance only.  Actual construction costs will vary depending on availability of materials and contractors used and the type of barrier removal utilized.